## Order_Summary (hidden)
Summary
| Items | Size | Qty | In Stock | Order Total | Unit | Part Number | Model Number | Description
| Line wire | 8 AWG-Black | #REF! |  | #REF! | ft. |  | Southwire 63949205 | Must have THHN insulation
|  | 12 AWG-Black | #REF! |  | #REF! | ft. |  | Encore Wire 106100801440 | Must have THHN insulation
|  | 14 AWG-Black | #REF! |  | #REF! | ft. | RC-WI00-E1BK-L500-02 | Encore Wire 106100701440 | Must have THHN insulation
|  | 16 AWG-Black | #REF! |  | #REF! | ft. | RC-WI00-H1BK-L500-02 |  | Must have THHN insulation
|  | 18 AWG-Black | #REF! |  | #REF! | ft. | RC-WI00-I1BK-L500-02 |  | Must have THHN insulation
| Control wire | 18 AWG-Red | #REF! |  | #REF! | ft. | RC-WI00-I1RD-L500-02 | Encore Wire 106100503440 | Must have THHN insulation
|  | 18 AWG-Blue | #REF! |  | #REF! | ft. | RC-WI00-I1BL-L500-02 |  | Must have THHN insulation
| Nichrome wire | 18 AWG | #REF! |  | #REF! | ft. | RM-WI00-NICR-18GA-01 | Remington Industries 18N80 | https://www.remingtonindustries.com/uninsulated-wire/nichrome-wire/nickel-chromium-resistance-wire-nichrome-80-18-awg-7-lengths-available/
|  | 20 AWG | #REF! |  | #REF! | ft. | RM-WI00-NICR-20GA-01 | Remington Industries 20N80 | https://www.remingtonindustries.com/uninsulated-wire/nichrome-wire/nickel-chromium-resistance-wire-nichrome-80-20-awg-7-lengths-available/
|  | 22 AWG | #REF! |  | #REF! | ft. | RM-WI00-NICR-22GA-01 | Remington Industries 22N80 | https://www.remingtonindustries.com/uninsulated-wire/nichrome-wire/nickel-chromium-resistance-wire-nichrome-80-22-awg-7-lengths-available/
|  | 24 AWG | #REF! |  | #REF! | ft. | RM-WI00-NICR-24GA-01 | Remington Industries 24N80 | https://www.remingtonindustries.com/uninsulated-wire/nichrome-wire/nickel-chromium-resistance-wire-nichrome-80-24-awg-7-lengths-available/
| Ceramics | - | #REF! |  | #REF! | # | HDW0065 |  | Ceramic/Porcelain Insulator Bushing Spacers (infraredheaters.com)
| Threaded crimp heads | - | #REF! |  | #REF! | # | HDW0073 |  | Crimphead10-32-100 Threaded Crimp Heads (morelectricheating.com)
| Ceramics (Plug and Cap) | - | #REF! |  | #REF! | # | HDW0066 |  | Ceramic/Porcelain Insulator Bushing Spacers (infraredheaters.com)
| Knife Edge Disconnect |  | #REF! |  | #REF!
| Standard Disconnect | 25 Amps | #REF! |  | #REF! | # | ELE0045 | MekTronics MKD-S225-31309MB34RDYR | https://www.mek-tronics.com/images/pdf/rotary-disconnect.pdf
|  | 40 Amps | #REF! |  | #REF! |  | ELE0046 | RS 466-283 | https://us.rs-online.com/product/rs-pro/466283/70822695/
| Fuse block | 30 Amps | #REF! |  | #REF! | # | ELE0041 | Bussmann T60030-3CR | https://www.grainger.com/product/BUSSMANN-Fuse-Block-Fits-Industrial-1CP58
|  | 60 Amps | #REF! |  | #REF! | # | ELE0042 | Bussmann T60060-3CR | https://www.grainger.com/product/BUSSMANN-Fuse-Block-Fits-Industrial-1DT33
| Fuse | 2 Amps | #REF! |  | #REF! |  | ELE0051
|  | 6 Amps | #REF! |  | #REF! | # | ELE0035 | Bussmann JJS-6 | https://www.grainger.com/product/BUSSMANN-Fuse-6-A-Amps-6F475
|  | 10 Amps | #REF! |  | #REF! | # | ELE0036 | Bussmann JJS-10 | https://www.grainger.com/product/BUSSMANN-Fuse-10-A-Amps-6F476
|  | 15 Amps | #REF! |  | #REF! | # | ELE0037 | Bussmann JJS-15 | https://www.grainger.com/product/BUSSMANN-Fuse-15-A-Amps-6F477
|  | 20 Amps | #REF! |  | #REF! | # | ELE0038 | Bussmann JJS-20 | https://www.grainger.com/product/BUSSMANN-Fuse-20-A-Amps-6F478
|  | 25 Amps | #REF! |  | #REF!
|  | 30 Amps | #REF! |  | #REF! | # | ELE0039 | Bussmann JJS-30 | https://www.grainger.com/product/BUSSMANN-Fuse-30-A-Amps-6F480
|  | 45 Amps | #REF! |  | #REF! | # | ELE0040 | Bussmann JJS-45 | https://www.grainger.com/product/BUSSMANN-Fuse-45-A-Amps-6F483
| Contactor | 25 Amps | #REF! |  | #REF! | # | ELE0033 | Schneider DPE18B7 | https://www.se.com/us/en/product/DPE18B7/iec-contactoreasy-tesys-dpenonreversing18a3p7-5hp-at-480v-ac24v-50-60hz-coil/
|  | 40 Amps | #REF! |  | #REF! | # | ELE0034 | Schneider DPE32B7 | https://www.se.com/us/en/product/DPE32B7/iec-contactoreasy-tesys-dpenonreversing32a3p15hp-at-480v-ac24v-50-60hz-coil/
| SCR | 25 Amps | #REF! |  | #REF! | # | ELE0031 (NOTE WE CAN USE THE 40 AMP VERSION FOR THIS ONE, SINCE WE HAVE STOCK) |  | Altran Magnetics
|  | 40 Amps | #REF! |  | #REF! | # | ELE0030 | 2xASR-SN480D40ZW-L+ASR-HS3A150+PWM Board (46112010001) | -
|  | 60 Amps | #REF! |  | #REF! | # | ELE0029
| Transformer | 50 VA | #REF! |  | #REF! | # | PC-XF00-PMS0-5000-01 | Intec- 5041MWCB-D, 50VA, class 2 transformer, primary 120, 240, 277, or 480V, secondary 24V | https://www.controlsystemsusa.com/controlsystemsusa/product.asp?pid=332-INTEC_5041MWCB-D_control_transformers_120240277480_to_24_vac
| Pressure Switch | - | #REF! |  | #REF! | # | ELE0047 |  | https://www.grainger.com/product/CLEVELAND-CONTROLS-Air-Sensing-Switch-Adj-6XPX7
| Manual thermal reset | - | #REF! |  | #REF! | # | ELE0043 | Selco Products Co- SE-L160M, 120/240VAC, 25A resistive, open @ 160°F ± 11°F, manual reset | https://us.rs-online.com/product/selco/se-l160m/70306716/
| Auto thermal reset | - | #REF! |  | #REF! | # | ELE0044 | Selco Products Co- SE-L120, 120/240VAC, 25A resistive, open @ 120°F ± 7°F, close @ 106°F ± 9°F | https://us.rs-online.com/product/selco/se-l120/70098733/?keyword=se-l120
| Ground lug | 12/14 AWG | #REF! |  | #REF! | # | PC-GL00-1110-0000-01 |  | Ground Lug, 1 mt, 1 sc, 6str
Did we change the useof these? | Fork terminals | 12-10 AWG | #REF! |  | #REF! | # | PC-TF00-FEMA-12GA-01 |  | https://www.elliottelectric.com/P/Item/TAB/10RC10FL/
| Ring terminals | 12-10 AWG | #REF! |  | #REF! | # | CNR0003 |  | https://www.elliottelectric.com/P/Item/TAB/10RC10E/
| Slide\Spade\Disconnector (female) terminals | 16-14 AWG | #REF! |  | #REF! | # | PC-CN00-FEMA-16GA-01 |  | https://www.elliottelectric.com/P/Item/TAB/14RB250FE/
| Butt connectors | 22-18 AWG | #REF! |  | #REF! | # | PC-CN00-BUTT-16GA-P1 |  | https://www.elliottelectric.com/P/Item/TAB/2RA18XE/
| 8/32 screw | - | #REF! |  | #REF! | # | PM-SK00-8-32-5-GS |  | SCREW, 8-32 X .5" PPH,GVS
| 8/32 Star nuts | - | #REF! |  | #REF! | # | HDW0074 |  | NUT, 8-32, LOCKING, GVS
| 8/32 pem nuts |  | #REF! |  | #REF! | # | HDW0002 |  | PEM NUT,8-32,MIN THICK 0.056"
| Extension Spring | - | #REF! |  | #REF! | # | HDW0069 | 1330K29 | McMaster-Carr
| Rivet | - | #REF! |  | #REF! | # | PM-HD00-115A-935C-3E |  | RIVET SS 1/8"X3/16"-3/8" LENGTH
| Rivet | - | #REF! |  | #REF! | # | PM-HD00-115A-935C-3M |  | RIVET 3/16DIA,GRIP.126/.187,SS
| Hinges | - | #REF! |  | #REF! | # | PM-HG00-060G-0100-01 |  | Hinge, W0.75xL2.00, 0.125pin
| Grommet | - | #REF! |  | #REF! | # | PC-BU00-D700-0000-P1 |  | 7/8" SNAP-IN BUSHING GROMMET
| Pitot Tube | - | #REF! |  | #REF! | # | PT-HD00-115B-1C49-F7 |  | GOL16,PITOT TUBE,TRAILING,SS
| Self Tapping Screws | - | #REF! |  | #REF! | # | PT-SC00-SAD5-L013-01 |  | TEK SCREW, ZINC, 10 X 1/2"
| 10/32 Star Nuts | - | #REF! |  | #REF! | # | HDW0045 |  | NUT,10-32,STEEL,W TOOTH WASHER

## Coil Calculator
Resistance | 153.6 | [11 empty] | Wye Connection |  |  |  | Delta Connection
Unit Height | 10 | [11 empty] | Line Voltage | 480 | Phase | 3 | Line Voltage | 480 | Phase | 3
Unit Width | 15 | [11 empty] | Phase Voltage | 277.1281 |  |  | Phase Voltage | 480
No. of Passes | 16 | [11 empty] | Power (kw) | 1.5 |  |  | Power (kW) | 1.5
Distance between Passes | 0.625 | [11 empty] | Resitance per wire (3) | 153.6 |  |  | Resistance per Wire (3) | 460.8
Desired Streched Length of Coil (in) | 237.4524 | [11 empty] | Power Factor | 1 |  |  | Power Factor | 1
Pitch (Linear Distance (in)/Turn) | 0.17 | [11 empty] | Line Current | 1.8042 |  |  | Line Current | 1.8042
Coil Wounding Diameter (in) | 0.25 | [11 empty] | Phase Current | 1.8042 |  |  | Phase Current | 1.0417
Estimated UnWounded Length (in) | 1122.4319
Gage AWG | Diameter (in) | Resistance at 68F Ω/ft | Resistance at 68F Ω/lb | Weight lb/1000 ft | Surface Area in2/ft | in2/Ω at 68F | Unwound Length (in) | Unstretch Wounded Length (in) | Actual Streched Length of Coil (in) | No. of passes possible | Actual Passes | Actual Pitch
1 | 0.2893 | 0.0078 | 0.0324 | 239.7906 | 10.9062 | 1404.2646 | 236307.6923 | 81678.6116 | 49991.3058 | 3341.0154 | 3341 | 0.0007892
2 | 0.2576 | 0.0098 | 0.0515 | 190.1623 | 9.7123 | 991.7162 | 188081.6327 | 58615.9438 | 39788.9985 | 2659.2023 | 2659 | 0.00099156
3 | 0.2294 | 0.0123 | 0.0819 | 150.8054 | 8.649 | 700.3673 | 149853.6585 | 42013.968 | 31701.8036 | 2118.7407 | 2118 | 0.0012445
4 | 0.2043 | 0.0156 | 0.1302 | 119.5939 | 7.7022 | 494.6117 | 118153.8462 | 29744.6643 | 24995.6529 | 1670.5733 | 1670 | 0.0015784
5 | 0.1819 | 0.0196 | 0.207 | 94.8422 | 6.859 | 349.3034 | 94040.8163 | 21218.4259 | 19894.4992 | 1329.6668 | 1329 | 0.0019831
6 | 0.162 | 0.0248 | 0.3292 | 75.2131 | 6.1081 | 246.6842 | 74322.5806 | 15014.0713 | 15723.072 | 1050.8932 | 1050 | 0.0025093
7 | 0.1443 | 0.0312 | 0.5235 | 59.6466 | 5.4394 | 174.2127 | 59076.9231 | 10675.4272 | 12497.8264 | 835.3523 | 835 | 0.0031568
8 | 0.1285 | 0.0394 | 0.8323 | 47.3019 | 4.8439 | 123.032 | 46781.7259 | 7553.5861 | 9896.756 | 661.5245 | 661 | 0.0039865
9 | 0.1144 | 0.0496 | 1.3235 | 37.512 | 4.3136 | 86.8874 | 37161.2903 | 5356.3387 | 7861.536 | 525.5122 | 525 | 0.0050186
10 | 0.1019 | 0.0626 | 2.1044 | 29.7484 | 3.8414 | 61.3614 | 29444.0895 | 3788.4151 | 6228.9486 | 416.4075 | 416 | 0.0063341
11 | 0.0907 | 0.0789 | 3.3462 | 23.5915 | 3.4209 | 43.3345 | 23361.2167 | 2680.0079 | 4942.1063 | 330.4087 | 330 | 0.0079835
12 | 0.0808 | 0.0995 | 5.3206 | 18.7089 | 3.0464 | 30.6036 | 18524.6231 | 1895.7658 | 3918.9164 | 262.0297 | 262 | 0.010068
13 | 0.072 | 0.1255 | 8.4602 | 14.8368 | 2.7129 | 21.6128 | 14686.8526 | 1340.7694 | 3107.0294 | 207.7718 | 207 | 0.0127
13.5 | 0.0679 | 0.141 | 10.6681 | 13.2125 | 2.5601 | 18.1627 | 13072.3404 | 1125.9427 | 2765.4765 | 184.9461 | 184 | 0.014269
14 | 0.0641 | 0.1583 | 13.4522 | 11.7661 | 2.4159 | 15.2633 | 11643.7145 | 947.1485 | 2463.2482 | 164.7484 | 164 | 0.01602
14.5 | 0.0605 | 0.1777 | 16.9629 | 10.478 | 2.2798 | 12.8268 | 10372.538 | 796.6468 | 2194.3286 | 146.7767 | 146 | 0.017984
15 | 0.0571 | 0.1996 | 21.3899 | 9.3309 | 2.1514 | 10.7792 | 9234.4689 | 669.5969 | 1953.5681 | 130.6868 | 130 | 0.020202
15.5 | 0.0539 | 0.2241 | 26.9722 | 8.3094 | 2.0302 | 9.0585 | 8224.8996 | 563.1307 | 1739.9919 | 116.4137 | 116 | 0.022684
16 | 0.0508 | 0.2517 | 34.0114 | 7.3997 | 1.9159 | 7.6125 | 7323.0036 | 472.6683 | 1549.1942 | 103.6628 | 103 | 0.02548
16.5 | 0.048 | 0.2826 | 42.8876 | 6.5897 | 1.808 | 6.3973 | 6522.293 | 397.8708 | 1379.8025 | 92.3425 | 92 | 0.028612
17 | 0.0453 | 0.3174 | 54.0804 | 5.8683 | 1.7061 | 5.3761 | 5807.1834 | 334.3895 | 1228.5198 | 82.2323 | 82 | 0.032141
17.5 | 0.0427 | 0.3564 | 68.1942 | 5.2258 | 1.61 | 4.5179 | 5171.7172 | 280.7578 | 1094.0858 | 73.2482 | 73 | 0.036099
18 | 0.0403 | 0.4002 | 85.9914 | 4.6537 | 1.5194 | 3.7967 | 4605.6972 | 236.015 | 974.3433 | 65.2459 | 65 | 0.040546
18.5 | 0.038 | 0.4494 | 108.4333 | 4.1443 | 1.4338 | 3.1906 | 4101.4686 | 198.2099 | 867.6729 | 58.1172 | 58 | 0.045547
19 | 0.0359 | 0.5046 | 136.7321 | 3.6906 | 1.353 | 2.6813 | 3652.7943 | 166.7925 | 772.755 | 51.7739 | 51 | 0.051164
19.5 | 0.0339 | 0.5667 | 172.4163 | 3.2865 | 1.2768 | 2.2533 | 3252.5146 | 140.2571 | 688.0751 | 46.1148 | 46 | 0.057492
20 | 0.032 | 0.6363 | 217.4132 | 2.9268 | 1.2049 | 1.8936 | 2896.7468 | 117.9262 | 612.8119 | 41.085 | 41 | 0.064598
20.5 | 0.0302 | 0.7145 | 274.1534 | 2.6063 | 1.137 | 1.5913 | 2579.7061 | 99.1212 | 545.7413 | 36.6027 | 36 | 0.072601
21 | 0.0285 | 0.8024 | 345.7015 | 2.321 | 1.073 | 1.3373 | 2297.1087 | 83.3011 | 485.9574 | 32.6074 | 32 | 0.081624
21.5 | 0.0269 | 0.901 | 435.9222 | 2.0669 | 1.0126 | 1.1238 | 2045.727 | 70.0254 | 432.7771 | 29.0534 | 29 | 0.091783
22 | 0.0253 | 1.0118 | 549.6885 | 1.8406 | 0.9555 | 0.9444 | 1821.7039 | 58.6521 | 385.3846 | 25.8862 | 25 | 0.10325
22.5 | 0.0239 | 1.1362 | 693.1454 | 1.6391 | 0.9017 | 0.7936 | 1622.2496 | 49.3429 | 343.1897 | 23.0664 | 23 | 0.11621
23 | 0.0226 | 1.2758 | 874.0415 | 1.4597 | 0.8509 | 0.667 | 1444.7406 | 41.5555 | 305.6374 | 20.5568 | 20 | 0.13086
23.5 | 0.0213 | 1.4327 | 1102.1476 | 1.2999 | 0.803 | 0.5605 | 1286.522 | 34.8777 | 272.166 | 18.3199 | 18 | 0.14749
24 | 0.0201 | 1.6088 | 1389.7844 | 1.1576 | 0.7578 | 0.471 | 1145.6987 | 29.3113 | 242.3746 | 16.3289 | 16 | 0.16639
24.5 | 0.019 | 1.8066 | 1752.4883 | 1.0309 | 0.7151 | 0.3958 | 1020.2591 | 24.6744 | 215.8376 | 14.5555 | 14 | 0.18795
25 | 0.0179 | 2.0287 | 2209.8501 | 0.918 | 0.6748 | 0.3326 | 908.5621 | 20.7017 | 192.2079 | 12.9763 | 12 | 0.21265
25.5 | 0.0169 | 2.2781 | 2786.5735 | 0.8175 | 0.6368 | 0.2795 | 809.0953 | 17.4059 | 171.1655 | 11.5701 | 11 | 0.24112
26 | 0.0159 | 2.5581 | 3513.8094 | 0.728 | 0.6009 | 0.2349 | 720.5348 | 14.5839 | 152.4304 | 10.318 | 10 | 0.27414
26.5 | 0.015 | 2.8726 | 4430.8381 | 0.6483 | 0.5671 | 0.1974 | 641.6487 | 12.2524 | 135.7419 | 9.2028 | 9 | 0.31286
27 | 0.0142 | 3.2257 | 5587.1917 | 0.5773 | 0.5351 | 0.1659 | 571.4109 | 10.3294 | 120.883 | 8.2097 | 8 | 0.35883
27.5 | 0.0134 | 3.6223 | 7045.3288 | 0.5141 | 0.505 | 0.1394 | 508.848 | 8.6804 | 107.6477 | 7.3252 | 7 | 0.41439
28 | 0.0126 | 4.0676 | 8884.0082 | 0.4579 | 0.4766 | 0.1172 | 453.1419 | 7.2687 | 95.863 | 6.5377 | 6 | 0.48322
29 | 0.0113 | 5.1291 | 14126.1669 | 0.3631 | 0.4244 | 0.0827 | 359.3613 | 5.1698 | 76.0235 | 5.2118 | 5 | 0.6914
30 | 0.01 | 6.4677 | 22461.5494 | 0.2879 | 0.3779 | 0.0584 | 284.9854 | 3.6283 | 60.2892 | 4.1603 | 4 | 1.1835

## Notes & Tables (hidden)
Basis for Ampacity & Wire Size |  | \ADVAULT\Q-Drive\Area 51\Products\Electric Reheat\Documentation\Rashish\submittal\Electric Reheat Configurations.xls
Basis for Nichrome Wire |  | \ADVAULT\Q-Drive\Area 51\Products\Electric Reheat\Documentation\Rashish\BOM\Electric Reheat BOM 480V 10kW.xls
Fuse Sizes |  | Size | Ampacity |  | SSR (Amps) | 80% (Amps) | 50% @40c (Amp)
1 |  | 18 | 10 | Table 16.1 | 25 | 20 | 12.5
2 |  | 16 | 13 | Table 16.1 | 40 | 32 | 20
3 |  | 14 | 18 | Table 16.1 | 50 | 40 | 25
6 |  | 12 | 25 | Table 16.1 | 60 | 48 | 30
10 |  | 10 | 30 | Table 16.1 | 70 | 56 | 35
15 |  | 8 | 55 | NEC310-16
20 |  | 6 | 75 | NEC310-16
25 |  | 4 | 95 | NEC310-16
30 |  | 3 | 110 | NEC310-16
35 |  | 2 | 130 | NEC310-16
40 |  | 1 | 150 | NEC310-16
45
50
60
70
80
90
100
1100
125
150
175
200
225
250
300
350
400
450
500
600
800
[6 empty] | 80% | 50%
[5 empty] | 25 | 18 | 16 | 19.8
[5 empty] | 40 | 3 | 2
[5 empty] | 50 | 1 | 2
Line Current | 80% | 50% @40C | Column1 |  | 60 | 0 | 0
8.42 | 25 | 25 | 1 |  | 70 | 0 | 2
7.22 | 25 | 25 | 2
10.83 | 25 | 25 | 3
10.83 | 25 | 25 | 4 |  |  | =IF([@['#]]='Notes & Tables'!$F8,'Notes & Tables'!O8,0)
16.84 | 25 | 40 | 5 |  |  | =IF([@['#]]='Notes & Tables'!$F8,'Notes & Tables'!O8,0)

## Sheet1 (hidden)
LINE | TAG # | SIZE | HEATING TYPE | VOLTAGE | PHASE | ELECTRIC STAGING | kW | ΔT (°F) | MAX HEATING CFM | LINE WIRE AWG | FUSE AMPS | FUSES PER UNIT | FPM | COIL HANDING | CONNECTION TYPE | PASSES | UNIT WIDTH | FUSE BLOCK AMPS | DISCONNECT | DISCONNECT AMPS | CONTACTOR SIZE AMPS | SCR AMPS | DIP SWITCH ON | TRANSFORMER WIRE USED | FUSE BLOCK MODEL | CONTACTOR MODEL | DISCONNECT MODEL | SCR MODEL | LOCATION | COIL PN# FOR X3 | Column1
1 | VAV-45.3 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 2 | 30 | 230 | 14 | 15 | 1 | 202.8846 | Right | Parallel | 8 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3R0200SE6A
2 | VAV-45.4 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1.5 | 30 | 115 | 14 | 15 | 1 | 151.9231 | Right | Parallel | 8 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3R0150SE6A
3 | VAV-45.5 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1 | 30 | 100 | 14 | 10 | 1 | 100.9615 | Right | Single | 22 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3R0100SE5A
4 | VAV-50.4 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1 | 30 | 150 | 14 | 10 | 1 | 100.9615 | Right | Single | 22 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3R0100SE5A
5 | VAV-54.2 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1 | 30 | 100 | 14 | 10 | 1 | 100.9615 | Right | Single | 22 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3R0100SE5A
6 | VAV-54.3 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1 | 30 | 145 | 14 | 10 | 1 | 100.9615 | Right | Single | 22 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3R0100SE5A
7 | VAV-54.4 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1 | 30 | 115 | 14 | 10 | 1 | 100.9615 | Right | Single | 22 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3R0100SE5A
8 | VAV-54.6 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1 | 30 | 160 | 14 | 10 | 1 | 100.9615 | Right | Single | 22 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3R0100SE5A
9 | VAV-45.1 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1 | 30 | 120 | 14 | 10 | 1 | 100.9615 | Left | Single | 22 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3L0100SE5A
10 | VAV-45.2 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1 | 30 | 95 | 14 | 10 | 1 | 100.9615 | Left | Single | 22 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3L0100SE5A
11 | VAV-50.1 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1 | 30 | 120 | 14 | 10 | 1 | 100.9615 | Left | Single | 22 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3L0100SE5A
12 | VAV-50.2 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 4 | 30 | 100 | 10 | 30 | 1 | 404.8077 | Left | Parallel | 8 | Normal | 30 | STD | 40 | 40 | 40 | 3,5 |  | 60308T | DPE32B7 | 466-277 | SN480D40ZW | Upstream | ERU-F3L0400SA9A
13 | VAV-50.3 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1 | 30 | 125 | 14 | 10 | 1 | 100.9615 | Left | Single | 22 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3L0100SE5A
14 | VAV-50.5 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 2 | 30 | 200 | 14 | 15 | 1 | 202.8846 | Left | Parallel | 8 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3L0200SE6A
15 | VAV-50.6 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 2 | 30 | 200 | 14 | 15 | 1 | 202.8846 | Left | Parallel | 8 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3L0200SE6A
16 | VAV-50.7 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1 | 30 | 125 | 14 | 10 | 1 | 100.9615 | Left | Single | 22 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3L0100SE5A
17 | VAV-50.8 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 2 | 30 | 200 | 14 | 15 | 1 | 202.8846 | Left | Parallel | 8 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3L0200SE6A
18 | VAV-50.9 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1 | 30 | 130 | 14 | 10 | 1 | 100.9615 | Left | Single | 22 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3L0100SE5A
19 | VAV-54.1 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 1.5 | 30 | 150 | 14 | 15 | 1 | 151.9231 | Left | Parallel | 8 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3L0150SE6A
20 | VAV-54.5 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 2 | 30 | 200 | 14 | 15 | 1 | 202.8846 | Left | Parallel | 8 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3L0200SE6A
21 | VAV-54.7 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 2 | 30 | 210 | 14 | 15 | 1 | 202.8846 | Left | Parallel | 8 | Normal | 30 | STD | 25 | 25 | 25 | 3,5 |  | 60308T | DPE18B7 | 466-273 | SN480D40ZW | Upstream | ERU-F3L0200SE6A
22 | VAV-54.8 | Rectangular 10" x 15" | Electric Reheat | 208 | 1 | SCR | 5 | 30 | 450 | 8 | 35 | 1 | 506.7308 | Left | Parallel | 8 | Normal | 60 | STD | 40 | 40 | 40 | 3,5 |  | 60608T | DPE32B7 | 466-277 | SN480D40ZW | Upstream | ERU-F3L0500S8AA